## 00_说明
以典型零碳园区为背景的电-热-氢-储综合能源系统优化调度仿真——数据包说明
项目名称 | 以典型零碳园区为背景的电-热-氢-储综合能源系统优化调度仿真
案例背景 | 参考鄂尔多斯市伊金霍洛旗蒙苏经济开发区零碳产业园。公开资料显示该园区依托风、光、氢、储、车等产业链，园区企业绿电使用比例接近70%，并配套风光储一体化项目。
数据口径 | 真实园区背景 + 公开数据集/政策数据 + 典型负荷曲线重构 + 工程/文献参数假设 + 场景仿真。
重要说明 | 本数据包不是园区真实运行数据，不声称获得企业内部负荷或调度数据。24小时数据用于模型开发、仿真演示和论文/简历项目复现。
建议用法 | Codex可先用 03_24h输入数据 + 04_设备技术经济参数 + 05_场景设置 建立MILP日前优化调度模型。
版本 | v1.0，生成日期：2026-06-16

## 01_数据来源总表
数据类别 | 字段/参数 | 本项目采用方式 | 建议值或数据构造方法 | 数据属性 | 来源URL | 备注
园区背景 | 案例定位 | 采用鄂尔多斯零碳产业园作为真实工程背景 | 位于内蒙古鄂尔多斯市伊金霍洛旗蒙苏经济开发区；用于背景描述，不用于声明真实运行数据 | 真实公开背景 | https://www.ordos.gov.cn/xw_127672/jreeds/202504/t20250407_3780540.html | 公开报道可支撑风光氢储车、绿电比例、园区产业场景
园区背景 | 绿电比例 | 作为模型目标参考，不直接作为约束 | 园区企业绿电使用比例接近70% | 真实公开背景 | https://www.ndrc.gov.cn/fggz/hjyzy/tdftzh/202504/t20250409_1397120.html | 可用于设定新能源渗透率场景
园区背景 | 产业规模 | 作为案例背景，不参与优化 | 2024年蒙苏经开区实现工业总产值652.9亿元、入驻企业172家等 | 真实公开背景 | https://kjt.nmg.gov.cn/kjdt/mtjj/202504/t20250417_2704475.html | 只用于说明案例典型性
新能源数据 | 光伏/风电时序 | 优先用NASA POWER按经纬度下载；当前提供24h重构示例 | NASA POWER小时API参数：ALLSKY_SFC_SW_DWN、WS50M、T2M；再换算为PV/WT可发功率 | 公开数据源 + 重构 | https://power.larc.nasa.gov/api/temporal/hourly/point?parameters=ALLSKY_SFC_SW_DWN,WS50M,T2M&community=RE&longitude=109.75&latitude=39.57&start=20250101&end=20250102&format=JSON | 建议Codex后续用API拉取全年8760h
负荷数据 | 电负荷/热负荷 | 使用典型园区负荷曲线重构；可用OEDI建筑负荷数据校准形态 | 提供24h工业园区电负荷、冬季热负荷示例 | 重构/假设 | https://data.openei.org/submissions/4520 | OEDI是美国建筑负荷，不能声称为鄂尔多斯实测
电价 | 蒙西工商业分时电价 | 按蒙西大风季时段与峰平谷倍率构造 | 峰：06-08/18-22；谷：00-04/11-16；平：其他；峰=平*1.68，谷=平*0.48 | 政策公开 + 假设平段价 | https://fgw.xlgl.gov.cn/fgw/ywgz/jgsf/zcfg/2024042615402690396/index.html | 平段价取0.55元/kWh作为示例，可替换
碳排放 | 外购电排放因子 | 用于电网购电间接排放计算 | 内蒙古2023年省级电力平均CO2排放因子0.6479 kgCO2/kWh | 官方数据 | https://www.mee.gov.cn/xxgk2018/xxgk/xxgk01/202512/W020251231726284332528.pdf | 适合核算购电排放
碳排放 | 华北区域基准线因子 | 可用于减排项目/敏感性分析 | 华北区域OM=0.9531 tCO2/MWh，BM=0.3095 tCO2/MWh | 公开因子 | https://www.ccn.ac.cn/wp-content/uploads/2024%E5%B9%B4%E5%87%8F%E6%8E%92%E9%A1%B9%E7%9B%AE%E4%B8%AD%E5%9B%BD%E5%8C%BA%E5%9F%9F%E7%94%B5%E7%BD%91%E4%BA%8C%E6%B0%A7%E5%8C%96%E7%A2%B3%E5%9F%BA%E5%87%86%E7%BA%BF%E6%8E%92%E6%94%BE%E5%9B%A0%E5%AD%90.pdf | 内蒙古属于华北区域电网
碳足迹 | 发电类型碳足迹因子 | 可选用于全生命周期对比 | 2024年风电0.0324、光伏0.0520、燃气发电0.4503 kgCO2e/kWh | 官方数据 | https://www.mee.gov.cn/xxgk2018/xxgk/xxgk01/202510/W020251024569470952545.pdf | 如只做运行排放，可不计风光LCA
氢价 | 生产侧/消费侧氢价 | 用于售氢收益/氢价敏感性 | 2024年12月全国生产侧约28.0元/kg，消费侧约48.6元/kg | 公开报告 | https://www.nea.gov.cn/20250430/96022785b3a747248288ad1c57d3a025/83d863317f2f44edb605348e4de40993.pdf | 本项目基准售氢价可取35元/kg，敏感性20-50
电解槽 | 耗电量/效率 | 用于制氢量计算 | DOE PEM代表值55.2 kWh/kg H2；IRENA 2020约51.2 kWh/kg H2 | 文献参数 | https://www.hydrogen.energy.gov/docs/hydrogenprogramlibraries/pdfs/24005-clean-hydrogen-production-cost-pem-electrolyzer.pdf | 建议基准取52 kWh/kg H2，敏感性45-60
储能 | 成本/性能 | 用于技术经济参数 | NREL ATB提供发电与储能技术成本性能数据 | 公开数据集 | https://data.openei.org/submissions/6006 | 本项目用简化运行模型，投资成本可年化
热泵 | COP | 用于电转热关系 | IEA说明热泵通过电力转移热量；文献综述中PV-ASHP平均COP约3.75 | 公开资料/文献 | https://arxiv.org/abs/2102.09797 | 本项目基准COP取3.0，冬季可敏感性2.2-3.5
燃气锅炉 | 效率 | 用于气耗与排放 | 公开案例燃气锅炉效率95%、低位发热量33077.3 kJ/Nm3 | 文献案例 | https://eri.usst.edu.cn/html/2021/1/20210104.htm | 本项目基准效率取0.92-0.95

## 02_园区背景
项目 | 公开信息/采用方式 | 用于本项目的位置 | 来源URL
案例地点 | 内蒙古鄂尔多斯市伊金霍洛旗蒙苏经济开发区零碳产业园 | 作为真实园区背景 | https://www.ordos.gov.cn/xw_127672/jreeds/202504/t20250407_3780540.html
产业特征 | 光伏、光热、氢能、储能等企业；形成风光氢储车全产业链条 | 用于说明系统为什么包含风、光、氢、储、热 | https://www.ordos.gov.cn/xw_127672/jreeds/202504/t20250407_3780540.html
绿电比例 | 园区企业绿电使用比例接近70% | 用于设置新能源渗透率场景/验证方向 | https://www.ndrc.gov.cn/fggz/hjyzy/tdftzh/202504/t20250409_1397120.html
风光储项目 | 公开报道称配套建设38.5万千瓦风光储一体化项目 | 用于背景说明，不作为本仿真容量边界 | https://www.ordos.gov.cn/xw_127672/jreeds/202504/t20250407_3780540.html
污水循环 | 废水循环利用率达95%；工业废水零排项目日处理约5万吨 | 可作为后续拓展水-能耦合方向 | https://www.ordos.gov.cn/xw_127672/jreeds/202504/t20250407_3780540.html
科创平台 | 搭建鄂尔多斯新能源研究院、氢能关键装备检测实证研发中心等平台 | 用于说明研究院/设计院招聘匹配度 | https://www.ordos.gov.cn/xw_127672/jreeds/202504/t20250407_3780540.html
本项目边界 | 选取典型园区尺度，不复刻真实园区全量规模；示例风电10MW、光伏8MW、电储能5MW/10MWh、电解槽2MW | 作为可计算的缩放案例 | 本表设定

## 03_24h输入数据
hour | pv_cf | wind_cf | pv_available_kW | wind_available_kW | electric_load_kW | heat_load_kW | h2_load_kg | tou_period | electricity_price_yuan_per_kWh | gas_price_yuan_per_m3 | grid_emission_kgCO2_per_kWh | carbon_price_yuan_per_tCO2 | 说明 | heat_pump_cop | heat_pump_available_ratio | electrolyzer_kwh_per_kg | fuel_cell_kwh_per_kg
0 | 0 | 0.42 | 0 | 4200 | 5200 | 6200 | 15 | 谷 | 0.264 | 3 | 0.6479 | 62.4 | 24h示例：新能源曲线为典型晴天+大风季重构；负荷为工业园区冬季典型日重构 | 3 | 1 | 52 | 18
1 | 0 | 0.45 | 0 | 4500 | 5000 | 6100 | 15 | 谷 | 0.264 | 3 | 0.6479 | 62.4 | 24h示例：新能源曲线为典型晴天+大风季重构；负荷为工业园区冬季典型日重构 | 3 | 1 | 52 | 18
2 | 0 | 0.48 | 0 | 4800 | 4800 | 6000 | 15 | 谷 | 0.264 | 3 | 0.6479 | 62.4 | 24h示例：新能源曲线为典型晴天+大风季重构；负荷为工业园区冬季典型日重构 | 3 | 1 | 52 | 18
3 | 0 | 0.5 | 0 | 5000 | 4700 | 5900 | 15 | 谷 | 0.264 | 3 | 0.6479 | 62.4 | 24h示例：新能源曲线为典型晴天+大风季重构；负荷为工业园区冬季典型日重构 | 3 | 1 | 52 | 18
4 | 0 | 0.52 | 0 | 5200 | 4800 | 5800 | 20 | 平 | 0.55 | 3 | 0.6479 | 62.4 | 24h示例：新能源曲线为典型晴天+大风季重构；负荷为工业园区冬季典型日重构 | 3 | 1 | 52 | 18
5 | 0.02 | 0.5 | 160 | 5000 | 5200 | 6000 | 25 | 平 | 0.55 | 3 | 0.6479 | 62.4 | 24h示例：新能源曲线为典型晴天+大风季重构；负荷为工业园区冬季典型日重构 | 3 | 1 | 52 | 18
6 | 0.12 | 0.46 | 960 | 4600 | 6200 | 6500 | 40 | 峰 | 0.924 | 3 | 0.6479 | 62.4 | 24h示例：新能源曲线为典型晴天+大风季重构；负荷为工业园区冬季典型日重构 | 3 | 1 | 52 | 18
7 | 0.3 | 0.4 | 2400 | 4000 | 7000 | 7000 | 50 | 峰 | 0.924 | 3 | 0.6479 | 62.4 | 24h示例：新能源曲线为典型晴天+大风季重构；负荷为工业园区冬季典型日重构 | 3 | 1 | 52 | 18
8 | 0.55 | 0.36 | 4400 | 3600 | 7600 | 6800 | 55 | 平 | 0.55 | 3 | 0.6479 | 62.4 | 24h示例：新能源曲线为典型晴天+大风季重构；负荷为工业园区冬季典型日重构 | 3 | 1 | 52 | 18
9 | 0.75 | 0.32 | 6000 | 3200 | 8100 | 6000 | 55 | 平 | 0.55 | 3 | 0.6479 | 62.4 | 24h示例：新能源曲线为典型晴天+大风季重构；负荷为工业园区冬季典型日重构 | 3 | 1 | 52 | 18
10 | 0.88 | 0.3 | 7040 | 3000 | 8300 | 5200 | 45 | 平 | 0.55 | 3 | 0.6479 | 62.4 | 24h示例：新能源曲线为典型晴天+大风季重构；负荷为工业园区冬季典型日重构 | 3 | 1 | 52 | 18
11 | 0.95 | 0.28 | 7600 | 2800 | 8200 | 4800 | 35 | 谷 | 0.264 | 3 | 0.6479 | 62.4 | 24h示例：新能源曲线为典型晴天+大风季重构；负荷为工业园区冬季典型日重构 | 3 | 1 | 52 | 18
12 | 0.9 | 0.3 | 7200 | 3000 | 8000 | 4600 | 30 | 谷 | 0.264 | 3 | 0.6479 | 62.4 | 24h示例：新能源曲线为典型晴天+大风季重构；负荷为工业园区冬季典型日重构 | 3 | 1 | 52 | 18
13 | 0.78 | 0.34 | 6240 | 3400 | 7900 | 4600 | 30 | 谷 | 0.264 | 3 | 0.6479 | 62.4 | 24h示例：新能源曲线为典型晴天+大风季重构；负荷为工业园区冬季典型日重构 | 3 | 1 | 52 | 18
14 | 0.58 | 0.38 | 4640 | 3800 | 8000 | 4800 | 35 | 谷 | 0.264 | 3 | 0.6479 | 62.4 | 24h示例：新能源曲线为典型晴天+大风季重构；负荷为工业园区冬季典型日重构 | 3 | 1 | 52 | 18
15 | 0.35 | 0.42 | 2800 | 4200 | 8300 | 5200 | 40 | 谷 | 0.264 | 3 | 0.6479 | 62.4 | 24h示例：新能源曲线为典型晴天+大风季重构；负荷为工业园区冬季典型日重构 | 3 | 1 | 52 | 18
16 | 0.12 | 0.44 | 960 | 4400 | 8600 | 5700 | 50 | 平 | 0.55 | 3 | 0.6479 | 62.4 | 24h示例：新能源曲线为典型晴天+大风季重构；负荷为工业园区冬季典型日重构 | 3 | 1 | 52 | 18
17 | 0.02 | 0.47 | 160 | 4700 | 9000 | 6400 | 60 | 平 | 0.55 | 3 | 0.6479 | 62.4 | 24h示例：新能源曲线为典型晴天+大风季重构；负荷为工业园区冬季典型日重构 | 3 | 1 | 52 | 18
18 | 0 | 0.5 | 0 | 5000 | 8800 | 7000 | 50 | 峰 | 0.924 | 3 | 0.6479 | 62.4 | 24h示例：新能源曲线为典型晴天+大风季重构；负荷为工业园区冬季典型日重构 | 3 | 1 | 52 | 18
19 | 0 | 0.52 | 0 | 5200 | 8200 | 7200 | 35 | 峰 | 0.924 | 3 | 0.6479 | 62.4 | 24h示例：新能源曲线为典型晴天+大风季重构；负荷为工业园区冬季典型日重构 | 3 | 1 | 52 | 18
20 | 0 | 0.55 | 0 | 5500 | 7400 | 7000 | 25 | 峰 | 0.924 | 3 | 0.6479 | 62.4 | 24h示例：新能源曲线为典型晴天+大风季重构；负荷为工业园区冬季典型日重构 | 3 | 1 | 52 | 18
21 | 0 | 0.54 | 0 | 5400 | 6500 | 6800 | 20 | 峰 | 0.924 | 3 | 0.6479 | 62.4 | 24h示例：新能源曲线为典型晴天+大风季重构；负荷为工业园区冬季典型日重构 | 3 | 1 | 52 | 18
22 | 0 | 0.5 | 0 | 5000 | 5800 | 6500 | 15 | 平 | 0.55 | 3 | 0.6479 | 62.4 | 24h示例：新能源曲线为典型晴天+大风季重构；负荷为工业园区冬季典型日重构 | 3 | 1 | 52 | 18
23 | 0 | 0.46 | 0 | 4600 | 5400 | 6300 | 15 | 平 | 0.55 | 3 | 0.6479 | 62.4 | 24h示例：新能源曲线为典型晴天+大风季重构；负荷为工业园区冬季典型日重构 | 3 | 1 | 52 | 18

## 04_设备技术经济参数
类别 | 参数 | 符号/字段 | 单位 | 基准值 | 敏感性范围 | 来源属性 | 来源URL | 用途/备注
规模 | 风电装机 | wind_capacity_kW | kW | 10000 | 5,000-20,000 | 本项目缩放假设 | https://www.ordos.gov.cn/xw_127672/jreeds/202504/t20250407_3780540.html | 真实园区有更大规模风光储；仿真取10MW便于计算
规模 | 光伏装机 | pv_capacity_kW | kW | 8000 | 4,000-20,000 | 本项目缩放假设 | https://www.ordos.gov.cn/xw_127672/jreeds/202504/t20250407_3780540.html | 用于PV可发功率=装机*PV_CF
电储能 | 额定功率 | battery_power_kW | kW | 5000 | 2,000-10,000 | 工程假设/NREL ATB | https://data.openei.org/submissions/6006 | 充放电功率上限
电储能 | 额定容量 | battery_energy_kWh | kWh | 10000 | 4,000-30,000 | 工程假设/NREL ATB | https://data.openei.org/submissions/6006 | SOC上限
电储能 | 充电效率 | battery_eta_ch | - | 0.95 | 0.90-0.97 | 常用假设/NREL储能资料 | https://data.openei.org/submissions/6006 | SOC动态
电储能 | 放电效率 | battery_eta_dis | - | 0.95 | 0.90-0.97 | 常用假设/NREL储能资料 | https://data.openei.org/submissions/6006 | SOC动态
电储能 | 初始SOC | battery_initial_soc | kWh | 5000 | 20%-80%容量 | 本项目假设 | 本表设定 | 末端SOC可设为等于初始SOC
氢能 | 电解槽额定功率 | electrolyzer_power_kW | kW | 2000 | 1,000-10,000 | 工程假设/文献 | https://www.hydrogen.energy.gov/docs/hydrogenprogramlibraries/pdfs/24005-clean-hydrogen-production-cost-pem-electrolyzer.pdf | 耗电制氢上限
氢能 | 电解槽耗电量 | electrolyzer_kWh_per_kgH2 | kWh/kgH2 | 52 | 45-60 | DOE/IRENA | https://www.hydrogen.energy.gov/docs/hydrogenprogramlibraries/pdfs/24005-clean-hydrogen-production-cost-pem-electrolyzer.pdf | 制氢量=耗电量/该值
氢能 | 储氢容量 | h2_storage_capacity_kg | kg | 1000 | 300-5000 | 工程假设 | 本表设定 | 储氢罐库存上限
氢能 | 初始储氢量 | h2_storage_initial_kg | kg | 300 | 20%-80%容量 | 本项目假设 | 本表设定 | 可设末端等于初始
氢能 | 燃料电池额定功率 | fuel_cell_power_kW | kW | 1000 | 500-5000 | 工程假设/DOE | https://www.nea.gov.cn/20250430/96022785b3a747248288ad1c57d3a025/83d863317f2f44edb605348e4de40993.pdf | 氢转电上限
氢能 | 燃料电池电效率 | fuel_cell_kWh_per_kgH2 | kWh/kgH2 | 18 | 16-22 | 工程假设/DOE目标 | https://www.nea.gov.cn/20250430/96022785b3a747248288ad1c57d3a025/83d863317f2f44edb605348e4de40993.pdf | 发电量=耗氢量*该值
热力 | 热泵额定电功率 | heat_pump_power_kW | kW | 3000 | 1,000-6,000 | 工程假设 | https://www.iea.org/reports/the-future-of-heat-pumps/how-a-heat-pump-works | 耗电上限
热力 | 热泵COP | heat_pump_COP | - | 3 | 2.2-3.8 | IEA/文献综述 | https://arxiv.org/abs/2102.09797 | 供热=耗电*COP
热力 | 燃气锅炉最大供热 | gas_boiler_heat_kW | kWth | 8000 | 4,000-12,000 | 工程假设/锅炉文献 | https://eri.usst.edu.cn/html/2021/1/20210104.htm | 备用热源
热力 | 燃气锅炉效率 | gas_boiler_eff | - | 0.92 | 0.88-0.95 | 文献/工程假设 | https://eri.usst.edu.cn/html/2021/1/20210104.htm | 气耗=供热/(LHV*效率)
能源价格 | 平段电价 | flat_electricity_price | 元/kWh | 0.55 | 0.40-0.80 | 假设+蒙西分时倍率 | https://fgw.xlgl.gov.cn/fgw/ywgz/jgsf/zcfg/2024042615402690396/index.html | 峰谷按政策倍率生成
能源价格 | 天然气价格 | gas_price | 元/m3 | 3 | 2.0-4.5 | 假设 | 本表设定 | 用于燃气锅炉成本
能源价格 | 售氢价格 | h2_sale_price | 元/kg | 35 | 20-50 | 中国氢能发展报告 | https://www.nea.gov.cn/20250430/96022785b3a747248288ad1c57d3a025/83d863317f2f44edb605348e4de40993.pdf | 用于售氢收益/敏感性
碳价 | 碳价 | carbon_price | 元/tCO2 | 62.4 | 0-200 | 碳市场报告 | https://ceep.bit.edu.cn/docs//2026-01/f57b33752f304d539c4d990b10a6eb63.pdf | 基准值取2025全国碳市场均价
碳排放 | 购电排放因子 | grid_emission_factor | kgCO2/kWh | 0.6479 | 0.5306全国/0.6479内蒙古/0.9531华北OM | 官方 | https://www.mee.gov.cn/xxgk2018/xxgk/xxgk01/202512/W020251231726284332528.pdf | 主模型使用内蒙古省级平均因子
碳排放 | 天然气排放因子 | gas_emission_factor | kgCO2/m3 | 2.16 | 1.9-2.3 | IPCC/WRI常用近似 | https://eri.usst.edu.cn/html/2021/1/20210104.htm | 本项目运行排放估算用，后续可替换为国家核算指南
惩罚成本 | 弃风弃光惩罚 | curtail_penalty | 元/kWh | 0.1 | 0-0.5 | 模型假设 | 本表设定 | 引导提高消纳率，可做敏感性
运维成本 | 电池运维 | battery_om | 元/kWh throughput | 0.01 | 0.005-0.03 | 模型假设/NREL ATB | https://data.openei.org/submissions/6006 | 简化可变运维成本
运维成本 | 电解槽运维 | electrolyzer_om | 元/kgH2 | 1 | 0.5-3.0 | 模型假设 | https://www.hydrogen.energy.gov/docs/hydrogenprogramlibraries/pdfs/24005-clean-hydrogen-production-cost-pem-electrolyzer.pdf | 简化可变运维成本
运维成本 | 燃料电池运维 | fuel_cell_om | 元/kWh | 0.05 | 0.02-0.15 | 模型假设 | https://www.nea.gov.cn/20250430/96022785b3a747248288ad1c57d3a025/83d863317f2f44edb605348e4de40993.pdf | 简化可变运维成本
设备成本 | 风电投资成本 | wind_capex_cny_per_kw | 元/kW | 7547 | 4200-7600 | web source / second group: IRENA Renewable Power Generation Costs in 2024 | https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2025/Jul/IRENA_TEC_RPGC_in_2024_Summary_2025.pdf | IRENA 2024 onshore wind TIC 1041 USD/kW 折算
设备成本 | 光伏投资成本 | pv_capex_cny_per_kw | 元/kW | 5010 | 3500-5500 | web source / second group: IRENA Renewable Power Generation Costs in 2024 | https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2025/Jul/IRENA_TEC_RPGC_in_2024_Summary_2025.pdf | IRENA 2024 TIC 691 USD/kW 折算，模型可用中国低成本情景
设备成本 | 电池储能功率成本 | battery_power_capex_cny_per_kw | 元/kW | 800 | 500-1500 | web source / second group: CNESA Energy Storage Industry White Paper 2024 Summary | https://en.cnesa.org/s/CNESA-Energy-Storage-Industry-WhitePaper-2024Summary-Version.pdf | PCS/并网/BOP 估算，建议敏感性分析
设备成本 | 电池储能能量成本 | battery_energy_capex_cny_per_kwh | 元/kWh | 1000 | 600-1300 | web source / second group: CNESA Energy Storage Industry White Paper 2024 Summary; IRENA Renewable Power Generation Costs in 2024 | https://en.cnesa.org/s/CNESA-Energy-Storage-Industry-WhitePaper-2024Summary-Version.pdf; https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2025/Jul/IRENA_TEC_RPGC_in_2024_Summary_2025.pdf | CNESA 系统中标价 0.79元/Wh，IRENA全球储能 192 USD/kWh 交叉校验
设备成本 | 碱性电解槽投资成本 | electrolyzer_capex_cny_per_kw | 元/kW | 2200 | 1500-7250 | web source / second group: DOE Technical Targets for PEM Electrolysis; IRENA Green Hydrogen Cost Reduction | https://www.energy.gov/cmei/fuels/technical-targets-proton-exchange-membrane-electrolysis; https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2020/Dec/IRENA_Green_hydrogen_cost_2020.pdf | 中国低成本设备取低值，PEM/国际系统取高值
设备成本 | 燃料电池投资成本 | fuel_cell_capex_cny_per_kw | 元/kW | 6000 | 1200-12000 | web source / second group: DOE Heavy-Duty Fuel Cell System Cost 2023 | https://www.hydrogen.energy.gov/docs/hydrogenprogramlibraries/pdfs/review24/24004-hd-fuel-cell-system-cost-2023.pdf | 交通用 PEM 成本低于固定式系统，园区备用取中值
设备成本 | 储氢投资成本 | h2_storage_capex_cny_per_kg | 元/kgH2 | 3600 | 220-5100 | web source / second group: Hydrogen Storage and Transport: Technologies and Costs | https://escholarship.org/content/qt83p5k54m/qt83p5k54m_noSplash_8bb1326c13cfb9aa3d0d376ec26d3e06.pdf | 液氢大罐低，压缩储氢高；园区短周期可做敏感性
设备成本 | 热泵投资成本 | heat_pump_capex_cny_per_kw | 元/kWth | 3500 | 2600-4600 | web source / second group: IRENA Heat Pump Costs and Markets | https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2022/Nov/IRENA_Heat_Pumps_Costs_Markets_2022.pdf | IRENA 商业热泵成本折算
设备成本 | 燃气锅炉投资成本 | gas_boiler_capex_cny_per_kwth | 元/kWth | 500 | 300-800 | web source / second group: IEA industrial heat pump chart notes | https://www.iea.org/data-and-statistics/charts/energy-input-cost-ratio-of-industrial-heat-pumps-relative-to-current-market-benchmarks-in-selected-regions-2024-3 | 成本需后续用具体厂家报价替换
设备寿命 | 风电寿命 | wind_life_years | 年 | 20 | 20-25 | web source / second group: IRENA Renewable Power Generation Costs in 2024 | https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2025/Jul/IRENA_TEC_RPGC_in_2024_Summary_2025.pdf | 容量规划年化用
设备寿命 | 光伏寿命 | pv_life_years | 年 | 25 | 25-30 | web source / second group: IRENA Renewable Power Generation Costs in 2024 | https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2025/Jul/IRENA_TEC_RPGC_in_2024_Summary_2025.pdf | 容量规划年化用
设备寿命 | 电池寿命 | battery_life_years | 年 | 12 | 10-15 | web source / second group: CNESA Energy Storage Industry White Paper 2024 Summary | https://en.cnesa.org/s/CNESA-Energy-Storage-Industry-WhitePaper-2024Summary-Version.pdf | 取决于循环和日历衰减
设备寿命 | 电解槽寿命 | electrolyzer_life_years | 年 | 15 | 8-20 | web source / second group: DOE Technical Targets for PEM Electrolysis; IRENA Green Hydrogen Cost Reduction | https://www.energy.gov/cmei/fuels/technical-targets-proton-exchange-membrane-electrolysis; https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2020/Dec/IRENA_Green_hydrogen_cost_2020.pdf | 也可用 40,000-80,000 小时约束
设备寿命 | 储氢寿命 | h2_storage_life_years | 年 | 20 | 15-30 | web source / second group: Hydrogen Storage and Transport: Technologies and Costs | https://escholarship.org/content/qt83p5k54m/qt83p5k54m_noSplash_8bb1326c13cfb9aa3d0d376ec26d3e06.pdf | 压力容器需按检验周期校核
设备寿命 | 燃料电池寿命 | fuel_cell_life_years | 年 | 10 | 5-15 | web source / second group: DOE Heavy-Duty Fuel Cell System Cost 2023 | https://www.hydrogen.energy.gov/docs/hydrogenprogramlibraries/pdfs/review24/24004-hd-fuel-cell-system-cost-2023.pdf | DOE 重卡系统耐久目标 25,000h；固定式可更高
财务 | 折现率 | discount_rate | - | 0.06 | 0.04-0.08 | web source / second group: IRENA Renewable Power Generation Costs in 2024; RMI 2024 China Power Market Outlook | https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2025/Jul/IRENA_TEC_RPGC_in_2024_Summary_2025.pdf; https://rmi.org/app/uploads/dlm_uploads/2025/01/final-2024-China-Power-Market-Outlook-10-Key-Trends-for-Market-Players-2501117.pdf | 容量规划年化成本用
设备寿命 | 热泵寿命 | heat_pump_life_years | 年 | 15 | 15-18 | web source / IEA heat pump lifetime | https://www.iea.org/reports/the-future-of-heat-pumps/executive-summary | IEA assumes 15 years for air-to-air and 18 years for air-to-water heat pumps; model uses conservative 15 years
市场机制 | 余电上网价格 | grid_sell_price_cny_per_kwh | 元/kWh | 0.2829 | 0.2-0.45 | web source / second group: RMI 2024 China Power Market Outlook | https://rmi.org/app/uploads/dlm_uploads/2025/01/final-2024-China-Power-Market-Outlook-10-Key-Trends-for-Market-Players-2501117.pdf | 按蒙西煤电基准价/机制电价近似，现货和绿电交易需另行替换
市场机制 | 最大上网容量 | grid_export_limit_kw | kW | 50000 | 0-100000 | web source / second group: Frontiers in Energy Research: heavy equipment manufacturing industrial park IES | https://www.frontiersin.org/journals/energy-research/articles/10.3389/fenrg.2024.1448362/full | 按 200MW 接入能力的 25% 设置，可由并网批复替换
市场机制 | 最大购电容量 | max_grid_import_kw | kW | 200000 | 150000-250000 | web source / second group: Frontiers in Energy Research: heavy equipment manufacturing industrial park IES | https://www.frontiersin.org/journals/energy-research/articles/10.3389/fenrg.2024.1448362/full | 公开案例有 200MW capacity 和 150MW peak demand
市场机制 | 需量电费 | demand_charge_cny_per_kw_year | 元/kW·年 | 393.6 | 374.4-393.6 | web source / second group: 锡林郭勒盟发改委: 内蒙古西部电网销售电价和输配电价公示表 | https://fgw.xlgl.gov.cn/fgw/ywgz/jgsf/jfgs/jggs/2023112710530866099/index.html | 35kV/110kV 31.2元/kW·月，1-10kV 32.8元/kW·月
氢市场 | 外购氢价格 | h2_external_supply_cost | 元/kg | 48.6 | 28-56.4 | web source / second group: 国家能源局: 中国氢能发展报告(2025) | https://www.nea.gov.cn/20250430/96022785b3a747248288ad1c57d3a025/83d863317f2f44edb605348e4de40993.pdf | 消费侧价格作为兜底外购价，生产侧价格作为低值
氢市场 | 售氢价格 | h2_sale_price_reference | 元/kg | 45.7 | 28-56.4 | web source / second group: 国家能源局: 中国氢能发展报告(2025) | https://www.nea.gov.cn/20250430/96022785b3a747248288ad1c57d3a025/83d863317f2f44edb605348e4de40993.pdf | 示范城市群消费侧价作对外售价参考
能源价格 | 售氢启用 | h2_sale_enabled | - | 0 | 0-1 | second group model setting | https://www.nea.gov.cn/20250430/96022785b3a747248288ad1c57d3a025/83d863317f2f44edb605348e4de40993.pdf | Default disabled; set to 1 in hydrogen sale scenarios
政策约束 | 年碳排放上限 | annual_carbon_cap_kgco2 | kgCO2/年 | 350000000 | 1e+08-8e+08 | web source / second group: Surbana Jurong: Ordos' new net-zero industrial park; 生态环境部/国家统计局 2022年电力二氧化碳排放因子 | https://www.sjgroup.com/projects/ordos/; https://www.mee.gov.cn/xxgk2018/xxgk/xxgk01/202412/t20241226_1099413.html | 零碳园区约束场景，建议按基准排放削减率设置
碳排放 | 碳排放日上限 | carbon_emission_cap_kg | kgCO2/day | 958904.1096 |  | web source / second group: Surbana Jurong: Ordos' new net-zero industrial park; 生态环境部/国家统计局 2022年电力二氧化碳排放因子 | https://www.sjgroup.com/projects/ordos/; https://www.mee.gov.cn/xxgk2018/xxgk/xxgk01/202412/t20241226_1099413.html | Converted from annual_carbon_cap_kgco2 / 365 for 24h dispatch model
碳排放 | 碳超额惩罚 | carbon_cap_excess_penalty | CNY/kgCO2 | 0 | 0-10 | second group model setting | https://www.sjgroup.com/projects/ordos/; https://www.mee.gov.cn/xxgk2018/xxgk/xxgk01/202412/t20241226_1099413.html | Default records excess without penalizing; raise value to enforce the cap
政策约束 | 新能源最低消纳率 | renewable_min_consumption_rate | - | 0.9 | 0.9-0.98 | web source / second group: 国家能源局: 电力系统调节能力优化专项行动 | https://www.nea.gov.cn/20250117/7a37e1cc43e4477baa101671b7dc273f/c.html | 国家能源局提出 2025-2027 全国新能源利用率不低于90%
政策约束 | 容量规划最低绿电比例 | green_power_min_share | - | 0.5 | 0.3-0.8 | web source / policy scenario assumption | https://www.nea.gov.cn/20250117/7a37e1cc43e4477baa101671b7dc273f/c.html | Scenario assumption for capacity planning green power share
设备效率 | 天然气低位热值 | gas_lhv_kwh_per_m3 | kWh/m3 | 10.814 | 10.5-11 | web source / second group: 国家发改委工业其他行业企业温室气体核算方法与报告指南 | https://www.ndrc.gov.cn/xxgk/zcfb/tz/201511/W020190905506438889540.pdf | 38.931 MJ/m3 / 3.6
氢能 | 储氢逐时损耗率 | h2_storage_loss_rate_per_hour | - | 4.1667e-05 | 0-0.000208 | web source / second group: Hydrogen Storage and Transport: Technologies and Costs | https://escholarship.org/content/qt83p5k54m/qt83p5k54m_noSplash_8bb1326c13cfb9aa3d0d376ec26d3e06.pdf | Converted from hydrogen_storage_loss_per_day / 24
运维退化 | 电池退化成本 | battery_degradation_cost_cny_per_kwh | 元/kWh throughput | 0.1 | 0.06-0.2 | web source / second group: CNESA Energy Storage Industry White Paper 2024 Summary | https://en.cnesa.org/s/CNESA-Energy-Storage-Industry-WhitePaper-2024Summary-Version.pdf | 按储能成本/可用循环吞吐估算
运维成本 | battery degradation segment 1 width | battery_degradation_segment_1_width_rate | - | 0.2 |  | web source / second group: CNESA Energy Storage Industry White Paper 2024 Summary | https://en.cnesa.org/s/CNESA-Energy-Storage-Industry-WhitePaper-2024Summary-Version.pdf | Piecewise battery degradation throughput width: shallow
运维成本 | battery degradation segment 1 cost | battery_degradation_segment_1_cost_cny_per_kwh | CNY/kWh throughput | 0.05 |  | web source / second group: CNESA Energy Storage Industry White Paper 2024 Summary | https://en.cnesa.org/s/CNESA-Energy-Storage-Industry-WhitePaper-2024Summary-Version.pdf | Piecewise battery degradation cost: shallow
运维成本 | battery degradation segment 2 width | battery_degradation_segment_2_width_rate | - | 0.3 |  | web source / second group: CNESA Energy Storage Industry White Paper 2024 Summary | https://en.cnesa.org/s/CNESA-Energy-Storage-Industry-WhitePaper-2024Summary-Version.pdf | Piecewise battery degradation throughput width: normal
运维成本 | battery degradation segment 2 cost | battery_degradation_segment_2_cost_cny_per_kwh | CNY/kWh throughput | 0.1 |  | web source / second group: CNESA Energy Storage Industry White Paper 2024 Summary | https://en.cnesa.org/s/CNESA-Energy-Storage-Industry-WhitePaper-2024Summary-Version.pdf | Piecewise battery degradation cost: normal
运维成本 | battery degradation segment 3 width | battery_degradation_segment_3_width_rate | - | 0.5 |  | web source / second group: CNESA Energy Storage Industry White Paper 2024 Summary | https://en.cnesa.org/s/CNESA-Energy-Storage-Industry-WhitePaper-2024Summary-Version.pdf | Piecewise battery degradation throughput width: deep
运维成本 | battery degradation segment 3 cost | battery_degradation_segment_3_cost_cny_per_kwh | CNY/kWh throughput | 0.18 |  | web source / second group: CNESA Energy Storage Industry White Paper 2024 Summary | https://en.cnesa.org/s/CNESA-Energy-Storage-Industry-WhitePaper-2024Summary-Version.pdf | Piecewise battery degradation cost: deep
细化曲线 | 电解槽最小负荷率 | electrolyzer_min_load_rate | - | 0.15 | 0.05-0.3 | web source / second group: IRENA Green Hydrogen Cost Reduction | https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2020/Dec/IRENA_Green_hydrogen_cost_2020.pdf | 碱性 15%-100%，PEM 可更宽
氢能 | electrolyzer segment 1 min rate | electrolyzer_segment_1_min_rate | - | 0.15 |  | web source / second group: DOE Technical Targets for PEM Electrolysis; IRENA Green Hydrogen Cost Reduction | https://www.energy.gov/cmei/fuels/technical-targets-proton-exchange-membrane-electrolysis; https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2020/Dec/IRENA_Green_hydrogen_cost_2020.pdf | Piecewise electrolyzer load-rate lower bound
氢能 | electrolyzer segment 1 max rate | electrolyzer_segment_1_max_rate | - | 0.3 |  | web source / second group: DOE Technical Targets for PEM Electrolysis; IRENA Green Hydrogen Cost Reduction | https://www.energy.gov/cmei/fuels/technical-targets-proton-exchange-membrane-electrolysis; https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2020/Dec/IRENA_Green_hydrogen_cost_2020.pdf | Piecewise electrolyzer load-rate upper bound
氢能 | electrolyzer segment 1 kWh per kg | electrolyzer_segment_1_kwh_per_kg | kWh/kgH2 | 60 |  | web source / second group: DOE Technical Targets for PEM Electrolysis; IRENA Green Hydrogen Cost Reduction | https://www.energy.gov/cmei/fuels/technical-targets-proton-exchange-membrane-electrolysis; https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2020/Dec/IRENA_Green_hydrogen_cost_2020.pdf | Piecewise electrolyzer electricity consumption
氢能 | electrolyzer segment 2 min rate | electrolyzer_segment_2_min_rate | - | 0.3 |  | web source / second group: DOE Technical Targets for PEM Electrolysis; IRENA Green Hydrogen Cost Reduction | https://www.energy.gov/cmei/fuels/technical-targets-proton-exchange-membrane-electrolysis; https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2020/Dec/IRENA_Green_hydrogen_cost_2020.pdf | Piecewise electrolyzer load-rate lower bound
氢能 | electrolyzer segment 2 max rate | electrolyzer_segment_2_max_rate | - | 0.6 |  | web source / second group: DOE Technical Targets for PEM Electrolysis; IRENA Green Hydrogen Cost Reduction | https://www.energy.gov/cmei/fuels/technical-targets-proton-exchange-membrane-electrolysis; https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2020/Dec/IRENA_Green_hydrogen_cost_2020.pdf | Piecewise electrolyzer load-rate upper bound
氢能 | electrolyzer segment 2 kWh per kg | electrolyzer_segment_2_kwh_per_kg | kWh/kgH2 | 55 |  | web source / second group: DOE Technical Targets for PEM Electrolysis; IRENA Green Hydrogen Cost Reduction | https://www.energy.gov/cmei/fuels/technical-targets-proton-exchange-membrane-electrolysis; https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2020/Dec/IRENA_Green_hydrogen_cost_2020.pdf | Piecewise electrolyzer electricity consumption
氢能 | electrolyzer segment 3 min rate | electrolyzer_segment_3_min_rate | - | 0.6 |  | web source / second group: DOE Technical Targets for PEM Electrolysis; IRENA Green Hydrogen Cost Reduction | https://www.energy.gov/cmei/fuels/technical-targets-proton-exchange-membrane-electrolysis; https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2020/Dec/IRENA_Green_hydrogen_cost_2020.pdf | Piecewise electrolyzer load-rate lower bound
氢能 | electrolyzer segment 3 max rate | electrolyzer_segment_3_max_rate | - | 0.9 |  | web source / second group: DOE Technical Targets for PEM Electrolysis; IRENA Green Hydrogen Cost Reduction | https://www.energy.gov/cmei/fuels/technical-targets-proton-exchange-membrane-electrolysis; https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2020/Dec/IRENA_Green_hydrogen_cost_2020.pdf | Piecewise electrolyzer load-rate upper bound
氢能 | electrolyzer segment 3 kWh per kg | electrolyzer_segment_3_kwh_per_kg | kWh/kgH2 | 51 |  | web source / second group: DOE Technical Targets for PEM Electrolysis; IRENA Green Hydrogen Cost Reduction | https://www.energy.gov/cmei/fuels/technical-targets-proton-exchange-membrane-electrolysis; https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2020/Dec/IRENA_Green_hydrogen_cost_2020.pdf | Piecewise electrolyzer electricity consumption
氢能 | electrolyzer segment 4 min rate | electrolyzer_segment_4_min_rate | - | 0.9 |  | web source / second group: DOE Technical Targets for PEM Electrolysis; IRENA Green Hydrogen Cost Reduction | https://www.energy.gov/cmei/fuels/technical-targets-proton-exchange-membrane-electrolysis; https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2020/Dec/IRENA_Green_hydrogen_cost_2020.pdf | Piecewise electrolyzer load-rate lower bound
氢能 | electrolyzer segment 4 max rate | electrolyzer_segment_4_max_rate | - | 1 |  | web source / second group: DOE Technical Targets for PEM Electrolysis; IRENA Green Hydrogen Cost Reduction | https://www.energy.gov/cmei/fuels/technical-targets-proton-exchange-membrane-electrolysis; https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2020/Dec/IRENA_Green_hydrogen_cost_2020.pdf | Piecewise electrolyzer load-rate upper bound
氢能 | electrolyzer segment 4 kWh per kg | electrolyzer_segment_4_kwh_per_kg | kWh/kgH2 | 54 |  | web source / second group: DOE Technical Targets for PEM Electrolysis; IRENA Green Hydrogen Cost Reduction | https://www.energy.gov/cmei/fuels/technical-targets-proton-exchange-membrane-electrolysis; https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2020/Dec/IRENA_Green_hydrogen_cost_2020.pdf | Piecewise electrolyzer electricity consumption
细化曲线 | 燃料电池最小负荷率 | fuel_cell_min_load_rate | - | 0.2 | 0.1-0.3 | web source / second group: DOE Heavy-Duty Fuel Cell System Cost 2023 | https://www.hydrogen.energy.gov/docs/hydrogenprogramlibraries/pdfs/review24/24004-hd-fuel-cell-system-cost-2023.pdf | 用于避免小负荷低效运行
氢能 | fuel cell segment 1 min rate | fuel_cell_segment_1_min_rate | - | 0.2 |  | web source / second group: DOE Heavy-Duty Fuel Cell System Cost 2023 | https://www.hydrogen.energy.gov/docs/hydrogenprogramlibraries/pdfs/review24/24004-hd-fuel-cell-system-cost-2023.pdf | Piecewise fuel-cell load-rate lower bound
氢能 | fuel cell segment 1 max rate | fuel_cell_segment_1_max_rate | - | 0.3 |  | web source / second group: DOE Heavy-Duty Fuel Cell System Cost 2023 | https://www.hydrogen.energy.gov/docs/hydrogenprogramlibraries/pdfs/review24/24004-hd-fuel-cell-system-cost-2023.pdf | Piecewise fuel-cell load-rate upper bound
氢能 | fuel cell segment 1 kWh per kg | fuel_cell_segment_1_kwh_per_kg | kWh/kgH2 | 16 |  | web source / second group: DOE Heavy-Duty Fuel Cell System Cost 2023 | https://www.hydrogen.energy.gov/docs/hydrogenprogramlibraries/pdfs/review24/24004-hd-fuel-cell-system-cost-2023.pdf | Piecewise fuel-cell electricity output
氢能 | fuel cell segment 2 min rate | fuel_cell_segment_2_min_rate | - | 0.3 |  | web source / second group: DOE Heavy-Duty Fuel Cell System Cost 2023 | https://www.hydrogen.energy.gov/docs/hydrogenprogramlibraries/pdfs/review24/24004-hd-fuel-cell-system-cost-2023.pdf | Piecewise fuel-cell load-rate lower bound
氢能 | fuel cell segment 2 max rate | fuel_cell_segment_2_max_rate | - | 0.6 |  | web source / second group: DOE Heavy-Duty Fuel Cell System Cost 2023 | https://www.hydrogen.energy.gov/docs/hydrogenprogramlibraries/pdfs/review24/24004-hd-fuel-cell-system-cost-2023.pdf | Piecewise fuel-cell load-rate upper bound
氢能 | fuel cell segment 2 kWh per kg | fuel_cell_segment_2_kwh_per_kg | kWh/kgH2 | 18.5 |  | web source / second group: DOE Heavy-Duty Fuel Cell System Cost 2023 | https://www.hydrogen.energy.gov/docs/hydrogenprogramlibraries/pdfs/review24/24004-hd-fuel-cell-system-cost-2023.pdf | Piecewise fuel-cell electricity output
氢能 | fuel cell segment 3 min rate | fuel_cell_segment_3_min_rate | - | 0.6 |  | web source / second group: DOE Heavy-Duty Fuel Cell System Cost 2023 | https://www.hydrogen.energy.gov/docs/hydrogenprogramlibraries/pdfs/review24/24004-hd-fuel-cell-system-cost-2023.pdf | Piecewise fuel-cell load-rate lower bound
氢能 | fuel cell segment 3 max rate | fuel_cell_segment_3_max_rate | - | 0.9 |  | web source / second group: DOE Heavy-Duty Fuel Cell System Cost 2023 | https://www.hydrogen.energy.gov/docs/hydrogenprogramlibraries/pdfs/review24/24004-hd-fuel-cell-system-cost-2023.pdf | Piecewise fuel-cell load-rate upper bound
氢能 | fuel cell segment 3 kWh per kg | fuel_cell_segment_3_kwh_per_kg | kWh/kgH2 | 19.5 |  | web source / second group: DOE Heavy-Duty Fuel Cell System Cost 2023 | https://www.hydrogen.energy.gov/docs/hydrogenprogramlibraries/pdfs/review24/24004-hd-fuel-cell-system-cost-2023.pdf | Piecewise fuel-cell electricity output
氢能 | fuel cell segment 4 min rate | fuel_cell_segment_4_min_rate | - | 0.9 |  | web source / second group: DOE Heavy-Duty Fuel Cell System Cost 2023 | https://www.hydrogen.energy.gov/docs/hydrogenprogramlibraries/pdfs/review24/24004-hd-fuel-cell-system-cost-2023.pdf | Piecewise fuel-cell load-rate lower bound
氢能 | fuel cell segment 4 max rate | fuel_cell_segment_4_max_rate | - | 1 |  | web source / second group: DOE Heavy-Duty Fuel Cell System Cost 2023 | https://www.hydrogen.energy.gov/docs/hydrogenprogramlibraries/pdfs/review24/24004-hd-fuel-cell-system-cost-2023.pdf | Piecewise fuel-cell load-rate upper bound
氢能 | fuel cell segment 4 kWh per kg | fuel_cell_segment_4_kwh_per_kg | kWh/kgH2 | 18.5 |  | web source / second group: DOE Heavy-Duty Fuel Cell System Cost 2023 | https://www.hydrogen.energy.gov/docs/hydrogenprogramlibraries/pdfs/review24/24004-hd-fuel-cell-system-cost-2023.pdf | Piecewise fuel-cell electricity output
备用价值 | 燃料电池备用容量价值 | fuel_cell_backup_value_cny_per_kw_year | 元/kW·年 | 300 | 100-1000 | web source / second group: LBNL outage cost literature review | https://eta-publications.lbl.gov/sites/default/files/erss_manuscript_preprint_0.pdf | 由停电损失和备用替代成本推导，需实测可靠性校准
备用价值 | 燃料电池备用上限 | fuel_cell_backup_reserve_kw | kW | 10000 | 0-50000 | second group model setting | https://eta-publications.lbl.gov/sites/default/files/erss_manuscript_preprint_0.pdf | Reserve capacity cap used by current second-group run script
备用价值 | 燃料电池必要备用 | fuel_cell_backup_required_kw | kW | 0 | 0-50000 | second group model setting | https://eta-publications.lbl.gov/sites/default/files/erss_manuscript_preprint_0.pdf | Default not mandatory; set by critical-load requirement when available
备用价值 | 停电损失 | value_of_lost_load_cny_per_kwh | 元/kWh | 55.2 | 15-350 | web source / second group: LBNL outage cost literature review | https://eta-publications.lbl.gov/sites/default/files/erss_manuscript_preprint_0.pdf | 7.61 USD/kWh * 7.25，工业差异极大
备用价值 | 年停电小时数 | annual_outage_hours | h/年 | 2 | 0.5-10 | web source / second group: LBNL outage cost literature review | https://eta-publications.lbl.gov/sites/default/files/erss_manuscript_preprint_0.pdf | 需用当地供电可靠性报告替换
细化曲线 | 热泵COP冬季 | heat_pump_cop_winter | - | 2.6 | 2.2-3.2 | web source / second group: NASA POWER Hourly API; IRENA Heat Pump Costs and Markets; IEA industrial heat pump chart notes | https://power.larc.nasa.gov/api/temporal/hourly/point?parameters=ALLSKY_SFC_SW_DWN,WS50M,T2M&community=RE&longitude=109.78&latitude=39.61&start=20240101&end=20241231&format=JSON&time-standard=LST; https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2022/Nov/IRENA_Heat_Pumps_Costs_Markets_2022.pdf; https://www.iea.org/data-and-statistics/charts/energy-input-cost-ratio-of-industrial-heat-pumps-relative-to-current-market-benchmarks-in-selected-regions-2024-3 | 低温空气源热泵按气温下修
细化曲线 | 热泵COP夏季 | heat_pump_cop_summer | - | 4 | 3.5-4.5 | web source / second group: IRENA Heat Pump Costs and Markets; IEA industrial heat pump chart notes | https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2022/Nov/IRENA_Heat_Pumps_Costs_Markets_2022.pdf; https://www.iea.org/data-and-statistics/charts/energy-input-cost-ratio-of-industrial-heat-pumps-relative-to-current-market-benchmarks-in-selected-regions-2024-3 | 夏季/过渡季低温差

## 05_场景设置
场景编号 | 场景名称 | 启用技术/机制 | 关键设置 | 主要观察指标 | 作用
S0 | 传统供能 | 外部电网 + 燃气锅炉 | wind=pv=battery=electrolyzer=storage=fuelcell=0 | 总成本、购电量、气耗、碳排放 | 作为基准场景
S1 | 新能源接入 | 风电 + 光伏 + 电网 + 锅炉 | 启用风光；不启用储能和氢能 | 弃风弃光、购电减少、碳排放下降 | 证明新能源低碳价值及消纳问题
S2 | 新能源+电储能 | S1 + 电化学储能 | 启用battery_power/energy | SOC、峰谷套利、弃电减少 | 证明储能短周期调节作用
S3 | 新能源+电储能+制氢 | S2 + 电解槽 + 储氢罐 | 启用electrolyzer和H2_storage | 制氢量、储氢量、弃电减少 | 证明绿氢承接富余新能源
S4 | 完整系统 | S3 + 燃料电池 + 热泵 | 启用fuel_cell和heat_pump | 氢转电、热泵替代锅炉、系统成本 | 形成主项目完整模型
S5 | 低碳调度 | S4 + 碳价机制 | carbon_price=62.4元/tCO2 | 碳成本、锅炉出力变化、热泵供热比例 | 体现低碳经济调度
S6 | 碳价敏感性 | 完整系统+不同碳价 | carbon_price=[0,50,100,150,200] | 碳排放、运行成本、锅炉/热泵出力 | 分析政策价格对调度影响
S7 | 氢价敏感性 | 完整系统+不同氢价 | h2_sale_price=[20,30,35,45,50] | 电解槽运行小时、售氢收益、制氢量 | 分析绿氢经济性
S8 | 储能容量敏感性 | 完整系统+不同储能容量 | battery_energy=[0,5000,10000,20000,30000] kWh | 弃电率、成本、SOC利用率 | 分析储能合理配置
S9 | 新能源渗透率敏感性 | 完整系统+不同风光容量 | wind/pv容量倍率=[0.5,1.0,1.5,2.0] | 消纳率、弃电量、碳排放、制氢需求 | 分析高比例新能源系统表现

## 06_来源URL
编号 | 来源名称 | URL | 用于哪些数据
R1 | 鄂尔多斯市人民政府：探访鄂尔多斯零碳产业园 | https://www.ordos.gov.cn/xw_127672/jreeds/202504/t20250407_3780540.html | 园区地点、绿电比例、38.5万千瓦风光储一体化项目、风光氢储车产业链
R2 | 国家发改委：探寻零碳园区的绿色密码 | https://www.ndrc.gov.cn/fggz/hjyzy/tdftzh/202504/t20250409_1397120.html | 零碳园区背景、鄂尔多斯绿电比例、风光资源利用
R3 | 内蒙古科技厅：鄂尔多斯蒙苏经济开发区报道 | https://kjt.nmg.gov.cn/kjdt/mtjj/202504/t20250417_2704475.html | 产业规模、企业数量、风光氢储一体化绿色工业体系
R4 | NASA POWER Hourly API | https://power.larc.nasa.gov/docs/services/api/temporal/hourly/ | 太阳辐照、风速、温度等小时数据获取方法
R5 | NASA POWER 鄂尔多斯示例API | https://power.larc.nasa.gov/api/temporal/hourly/point?parameters=ALLSKY_SFC_SW_DWN,WS50M,T2M&community=RE&longitude=109.75&latitude=39.57&start=20250101&end=20250102&format=JSON | 可直接用于Codex拉取示例地点数据
R6 | OEDI End-Use Load Profiles | https://data.openei.org/submissions/4520 | 典型建筑/园区负荷曲线校准来源
R7 | 锡林郭勒盟发改委：蒙西/蒙东工商业分时电价解读 | https://fgw.xlgl.gov.cn/fgw/ywgz/jgsf/zcfg/2024042615402690396/index.html | 蒙西峰平谷时段、峰谷倍率
R8 | 生态环境部：2023年电力二氧化碳排放因子 | https://www.mee.gov.cn/xxgk2018/xxgk/xxgk01/202512/W020251231726284332528.pdf | 内蒙古电力平均CO2排放因子0.6479 kgCO2/kWh
R9 | 生态环境部：2024年全国电力碳足迹因子 | https://www.mee.gov.cn/xxgk2018/xxgk/xxgk01/202510/W020251024569470952545.pdf | 风电、光伏、燃气发电碳足迹因子
R10 | 国家气候战略中心：2024区域电网基准线排放因子 | https://www.ccn.ac.cn/wp-content/uploads/2024%E5%B9%B4%E5%87%8F%E6%8E%92%E9%A1%B9%E7%9B%AE%E4%B8%AD%E5%9B%BD%E5%8C%BA%E5%9F%9F%E7%94%B5%E7%BD%91%E4%BA%8C%E6%B0%A7%E5%8C%96%E7%A2%B3%E5%9F%BA%E5%87%86%E7%BA%BF%E6%8E%92%E6%94%BE%E5%9B%A0%E5%AD%90.pdf | 华北区域OM/BM排放因子
R11 | 中国氢能发展报告（2025） | https://www.nea.gov.cn/20250430/96022785b3a747248288ad1c57d3a025/83d863317f2f44edb605348e4de40993.pdf | 氢价、氢能应用场景
R12 | DOE PEM Electrolyzer Clean Hydrogen Production Cost | https://www.hydrogen.energy.gov/docs/hydrogenprogramlibraries/pdfs/24005-clean-hydrogen-production-cost-pem-electrolyzer.pdf | 电解槽耗电量55.2 kWh/kgH2
R13 | IRENA Green Hydrogen Cost Reduction | https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2020/Dec/IRENA_Green_hydrogen_cost_2020.pdf | 电解槽效率/耗电量参考
R14 | NREL 2024 ATB | https://data.openei.org/submissions/6006 | 储能/发电成本性能参数
R15 | 燃气锅炉低氮排放经济性分析 | https://eri.usst.edu.cn/html/2021/1/20210104.htm | 燃气锅炉效率95%、天然气低位发热量
R16 | IEA Heat Pumps | https://www.iea.org/reports/the-future-of-heat-pumps/how-a-heat-pump-works | 热泵工作原理和低碳供热逻辑
R17 | ASHP系统综述 | https://arxiv.org/abs/2102.09797 | PV-ASHP平均COP约3.75等
S01 | Surbana Jurong: Ordos' new net-zero industrial park | https://www.sjgroup.com/projects/ordos/ | Ordos, Inner Mongolia; 73 km2; 100% zero-carbon energy supply; hydrogen and air-source heat-pump measures
S02 | Frontiers in Energy Research: heavy equipment manufacturing industrial park IES | https://www.frontiersin.org/journals/energy-research/articles/10.3389/fenrg.2024.1448362/full | 2 km2 industrial park, 50+ facilities, 200 MW capacity, 150 MW peak demand, 1.2 TWh electricity and 0.8 TWh thermal energy annually
S03 | NASA POWER Hourly API | https://power.larc.nasa.gov/api/temporal/hourly/point?parameters=ALLSKY_SFC_SW_DWN,WS50M,T2M&community=RE&longitude=109.78&latitude=39.61&start=20240101&end=20241231&format=JSON&time-standard=LST | Ordos point hourly ALLSKY_SFC_SW_DWN, WS50M, T2M, 2024, LST
S04 | 锡林郭勒盟发改委: 内蒙古西部电网销售电价和输配电价公示表 | https://fgw.xlgl.gov.cn/fgw/ywgz/jgsf/jfgs/jggs/2023112710530866099/index.html | 蒙西峰平谷时段、峰谷比价、尖峰/深谷规则、需量电价
S05 | 鄂尔多斯市发改委非居民管道天然气价格通知 | https://www.ordos.gov.cn/ordosml/szbm/sfzhggwyh_n/202605/t20260528_3900116.html | 2026-04-01 至 2026-10-31 非居民终端销售价格 2.952 元/m3
S06 | 生态环境部/国家统计局 2022年电力二氧化碳排放因子 | https://www.mee.gov.cn/xxgk2018/xxgk/xxgk01/202412/t20241226_1099413.html | 内蒙古省级电力平均二氧化碳排放因子 0.6849 kgCO2/kWh
S07 | 生态环境部: 2025年全国碳市场运行情况 | https://www.mee.gov.cn/ywgz/ydqhbh/wsqtkz/202601/t20260101_1139528.shtml | 2025 全年交易均价 62.36 元/tCO2，年底收盘价 74.63 元/tCO2
S08 | IRENA Renewable Power Generation Costs in 2024 | https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2025/Jul/IRENA_TEC_RPGC_in_2024_Summary_2025.pdf | 2024 PV TIC 691 USD/kW, onshore wind TIC 1041 USD/kW, battery storage 192 USD/kWh
S09 | CNESA Energy Storage Industry White Paper 2024 Summary | https://en.cnesa.org/s/CNESA-Energy-Storage-Industry-WhitePaper-2024Summary-Version.pdf | 2023 年底 2h LFP 储能系统平均中标价 0.79 元/Wh，部分集采低于 0.6 元/Wh
S10 | DOE Technical Targets for PEM Electrolysis | https://www.energy.gov/cmei/fuels/technical-targets-proton-exchange-membrane-electrolysis | PEM 2022 status: system efficiency 55 kWh/kg H2, uninstalled capital cost 1000 USD/kW, lifetime 40,000 h
S11 | IRENA Green Hydrogen Cost Reduction | https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2020/Dec/IRENA_Green_hydrogen_cost_2020.pdf | Alkaline system 50-78 kWh/kg H2 and 500-1000 USD/kW; PEM system 50-83 kWh/kg H2 and 700-1400 USD/kW
S12 | 国家能源局: 中国氢能发展报告(2025) | https://www.nea.gov.cn/20250430/96022785b3a747248288ad1c57d3a025/83d863317f2f44edb605348e4de40993.pdf | 2024年底生产侧 28.0 元/kg，消费侧 48.6 元/kg；内蒙古等为氢消费重点地区
S13 | IRENA Heat Pump Costs and Markets | https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2022/Nov/IRENA_Heat_Pumps_Costs_Markets_2022.pdf | Commercial air-air/air-water heat pump costs and COP values; e.g. 358-627 USD/kWth and COP around 3.9-4.2 in reported cases
S14 | IEA industrial heat pump chart notes | https://www.iea.org/data-and-statistics/charts/energy-input-cost-ratio-of-industrial-heat-pumps-relative-to-current-market-benchmarks-in-selected-regions-2024-3 | Assumed efficiencies: coal boilers 84%, natural gas boilers 87%, electric boilers 98%, heat pumps 350%
S15 | DOE Heavy-Duty Fuel Cell System Cost 2023 | https://www.hydrogen.energy.gov/docs/hydrogenprogramlibraries/pdfs/review24/24004-hd-fuel-cell-system-cost-2023.pdf | 275 kW PEM fuel cell system projected about 170 USD/kW at 50k units/year; 25,000 h durability target
S16 | Hydrogen Storage and Transport: Technologies and Costs | https://escholarship.org/content/qt83p5k54m/qt83p5k54m_noSplash_8bb1326c13cfb9aa3d0d376ec26d3e06.pdf | Liquid hydrogen large tank cost 30-50 USD/kgH2; compressed gas storage references included for sensitivity
S17 | 国家发改委工业其他行业企业温室气体核算方法与报告指南 | https://www.ndrc.gov.cn/xxgk/zcfb/tz/201511/W020190905506438889540.pdf | 天然气低位发热量、单位热值含碳量、碳氧化率用于推导约 2.16 kgCO2/m3
S18 | 国家能源局: 电力系统调节能力优化专项行动 | https://www.nea.gov.cn/20250117/7a37e1cc43e4477baa101671b7dc273f/c.html | 2025-2027 年全国新能源利用率不低于 90%
S19 | RMI 2024 China Power Market Outlook | https://rmi.org/app/uploads/dlm_uploads/2025/01/final-2024-China-Power-Market-Outlook-10-Key-Trends-for-Market-Players-2501117.pdf | I&C price components, capacity pricing, ancillary services and energy-storage market participation context
S20 | LBNL outage cost literature review | https://eta-publications.lbl.gov/sites/default/files/erss_manuscript_preprint_0.pdf | Industrial outage value examples include 7.61 USD/kWh in reviewed literature; use as sensitivity anchor

## 07_Codex使用说明
Codex开发任务拆解
任务 | 输入 | 输出 | 建议实现 | 备注
数据读取 | 03_24h输入数据、04_设备技术经济参数 | Python字典/Series | read_csv或read_excel读取 | 后续可替换为NASA POWER API自动下载
模型变量 | 每小时设备出力、SOC、储氢量、弃电量、购电量等 | Pyomo变量 | 按t=0..23建立连续变量，启停变量可后续增加 | 先LP，后MILP
目标函数 | 电价、气价、碳价、运维、弃电惩罚、售氢收益 | 最小总成本 | cost = grid + gas + om + curtail + carbon - h2_revenue | 保证单位一致
约束体系 | 设备参数+时序数据 | 电/热/氢平衡和设备边界 | 逐时电平衡、热平衡、氢平衡、SOC、储氢、设备功率上限 | 这是核心
场景管理 | 05_场景设置 | 多场景结果表 | 用scenario_config控制启用设备和参数倍率 | 先做S0-S5
结果可视化 | 优化结果 | 曲线图/柱状图 | 设备出力、SOC、储氢、成本、碳排放、消纳率 | 用于报告和简历
结果校验 | 功率平衡/边界/非负性 | 校验日志 | 检查每小时平衡残差、SOC范围、弃电计算 | 防止模型看似有解但物理错误