## Sheet1
category | name_cn | parameter | unit | value | sensitivity_range | source_attribute | source_url | description
规模 | 风电装机 | wind_capacity_kW | kW | 10000 | 5,000-20,000 | 本项目缩放假设 | https://www.ordos.gov.cn/xw_127672/jreeds/202504/t20250407_3780540.html | 真实园区有更大规模风光储；仿真取10MW便于计算
规模 | 光伏装机 | pv_capacity_kW | kW | 8000 | 4,000-20,000 | 本项目缩放假设 | https://www.ordos.gov.cn/xw_127672/jreeds/202504/t20250407_3780540.html | 用于PV可发功率=装机*PV_CF
电储能 | 额定功率 | battery_power_kW | kW | 5000 | 2,000-10,000 | 工程假设/NREL ATB | https://data.openei.org/submissions/6006 | 充放电功率上限
电储能 | 额定容量 | battery_energy_kWh | kWh | 10000 | 4,000-30,000 | 工程假设/NREL ATB | https://data.openei.org/submissions/6006 | SOC上限
电储能 | 充电效率 | battery_eta_ch | - | 0.95 | 0.90-0.97 | 常用假设/NREL储能资料 | https://data.openei.org/submissions/6006 | SOC动态
电储能 | 放电效率 | battery_eta_dis | - | 0.95 | 0.90-0.97 | 常用假设/NREL储能资料 | https://data.openei.org/submissions/6006 | SOC动态
电储能 | 初始SOC | battery_initial_soc | kWh | 5000 | 20%-80%容量 | 本项目假设 | 本表设定 | 末端SOC可设为等于初始SOC
氢能 | 电解槽额定功率 | electrolyzer_power_kW | kW | 2000 | 1,000-10,000 | 工程假设/文献 | https://www.hydrogen.energy.gov/docs/hydrogenprogramlibraries/pdfs/24005-clean-hydrogen-production-cost-pem-electrolyzer.pdf | 耗电制氢上限
氢能 | 电解槽耗电量 | electrolyzer_kWh_per_kgH2 | kWh/kgH2 | 52 | 45-60 | DOE/IRENA | https://www.hydrogen.energy.gov/docs/hydrogenprogramlibraries/pdfs/24005-clean-hydrogen-production-cost-pem-electrolyzer.pdf | 制氢量=耗电量/该值
氢能 | 储氢容量 | h2_storage_capacity_kg | kg | 1000 | 300-5000 | 工程假设 | 本表设定 | 储氢罐库存上限
氢能 | 初始储氢量 | h2_storage_initial_kg | kg | 300 | 20%-80%容量 | 本项目假设 | 本表设定 | 可设末端等于初始
氢能 | 燃料电池额定功率 | fuel_cell_power_kW | kW | 1000 | 500-5000 | 工程假设/DOE | https://www.nea.gov.cn/20250430/96022785b3a747248288ad1c57d3a025/83d863317f2f44edb605348e4de40993.pdf | 氢转电上限
氢能 | 燃料电池电效率 | fuel_cell_kWh_per_kgH2 | kWh/kgH2 | 18 | 16-22 | 工程假设/DOE目标 | https://www.nea.gov.cn/20250430/96022785b3a747248288ad1c57d3a025/83d863317f2f44edb605348e4de40993.pdf | 发电量=耗氢量*该值
热力 | 热泵额定电功率 | heat_pump_power_kW | kW | 3000 | 1,000-6,000 | 工程假设 | https://www.iea.org/reports/the-future-of-heat-pumps/how-a-heat-pump-works | 耗电上限
热力 | 热泵COP | heat_pump_COP | - | 3 | 2.2-3.8 | IEA/文献综述 | https://arxiv.org/abs/2102.09797 | 供热=耗电*COP
热力 | 燃气锅炉最大供热 | gas_boiler_heat_kW | kWth | 8000 | 4,000-12,000 | 工程假设/锅炉文献 | https://eri.usst.edu.cn/html/2021/1/20210104.htm | 备用热源
热力 | 燃气锅炉效率 | gas_boiler_eff | - | 0.92 | 0.88-0.95 | 文献/工程假设 | https://eri.usst.edu.cn/html/2021/1/20210104.htm | 气耗=供热/(LHV*效率)
设备成本 | 风电投资成本 | wind_capex_cny_per_kw | 元/kW | 7547 | 4200-7600 | web source / second group: IRENA Renewable Power Generation Costs in 2024 | https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2025/Jul/IRENA_TEC_RPGC_in_2024_Summary_2025.pdf | IRENA 2024 onshore wind TIC 1041 USD/kW 折算
设备成本 | 光伏投资成本 | pv_capex_cny_per_kw | 元/kW | 5010 | 3500-5500 | web source / second group: IRENA Renewable Power Generation Costs in 2024 | https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2025/Jul/IRENA_TEC_RPGC_in_2024_Summary_2025.pdf | IRENA 2024 TIC 691 USD/kW 折算，模型可用中国低成本情景
设备成本 | 电池储能功率成本 | battery_power_capex_cny_per_kw | 元/kW | 800 | 500-1500 | web source / second group: CNESA Energy Storage Industry White Paper 2024 Summary | https://en.cnesa.org/s/CNESA-Energy-Storage-Industry-WhitePaper-2024Summary-Version.pdf | PCS/并网/BOP 估算，建议敏感性分析
设备成本 | 电池储能能量成本 | battery_energy_capex_cny_per_kwh | 元/kWh | 1000 | 600-1300 | web source / second group: CNESA Energy Storage Industry White Paper 2024 Summary; IRENA Renewable Power Generation Costs in 2024 | https://en.cnesa.org/s/CNESA-Energy-Storage-Industry-WhitePaper-2024Summary-Version.pdf; https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2025/Jul/IRENA_TEC_RPGC_in_2024_Summary_2025.pdf | CNESA 系统中标价 0.79元/Wh，IRENA全球储能 192 USD/kWh 交叉校验
设备成本 | 碱性电解槽投资成本 | electrolyzer_capex_cny_per_kw | 元/kW | 2200 | 1500-7250 | web source / second group: DOE Technical Targets for PEM Electrolysis; IRENA Green Hydrogen Cost Reduction | https://www.energy.gov/cmei/fuels/technical-targets-proton-exchange-membrane-electrolysis; https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2020/Dec/IRENA_Green_hydrogen_cost_2020.pdf | 中国低成本设备取低值，PEM/国际系统取高值
设备成本 | 燃料电池投资成本 | fuel_cell_capex_cny_per_kw | 元/kW | 6000 | 1200-12000 | web source / second group: DOE Heavy-Duty Fuel Cell System Cost 2023 | https://www.hydrogen.energy.gov/docs/hydrogenprogramlibraries/pdfs/review24/24004-hd-fuel-cell-system-cost-2023.pdf | 交通用 PEM 成本低于固定式系统，园区备用取中值
设备成本 | 储氢投资成本 | h2_storage_capex_cny_per_kg | 元/kgH2 | 3600 | 220-5100 | web source / second group: Hydrogen Storage and Transport: Technologies and Costs | https://escholarship.org/content/qt83p5k54m/qt83p5k54m_noSplash_8bb1326c13cfb9aa3d0d376ec26d3e06.pdf | 液氢大罐低，压缩储氢高；园区短周期可做敏感性
设备成本 | 热泵投资成本 | heat_pump_capex_cny_per_kw | 元/kWth | 3500 | 2600-4600 | web source / second group: IRENA Heat Pump Costs and Markets | https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2022/Nov/IRENA_Heat_Pumps_Costs_Markets_2022.pdf | IRENA 商业热泵成本折算
设备成本 | 燃气锅炉投资成本 | gas_boiler_capex_cny_per_kwth | 元/kWth | 500 | 300-800 | web source / second group: IEA industrial heat pump chart notes | https://www.iea.org/data-and-statistics/charts/energy-input-cost-ratio-of-industrial-heat-pumps-relative-to-current-market-benchmarks-in-selected-regions-2024-3 | 成本需后续用具体厂家报价替换
设备寿命 | 风电寿命 | wind_life_years | 年 | 20 | 20-25 | web source / second group: IRENA Renewable Power Generation Costs in 2024 | https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2025/Jul/IRENA_TEC_RPGC_in_2024_Summary_2025.pdf | 容量规划年化用
设备寿命 | 光伏寿命 | pv_life_years | 年 | 25 | 25-30 | web source / second group: IRENA Renewable Power Generation Costs in 2024 | https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2025/Jul/IRENA_TEC_RPGC_in_2024_Summary_2025.pdf | 容量规划年化用
设备寿命 | 电池寿命 | battery_life_years | 年 | 12 | 10-15 | web source / second group: CNESA Energy Storage Industry White Paper 2024 Summary | https://en.cnesa.org/s/CNESA-Energy-Storage-Industry-WhitePaper-2024Summary-Version.pdf | 取决于循环和日历衰减
设备寿命 | 电解槽寿命 | electrolyzer_life_years | 年 | 15 | 8-20 | web source / second group: DOE Technical Targets for PEM Electrolysis; IRENA Green Hydrogen Cost Reduction | https://www.energy.gov/cmei/fuels/technical-targets-proton-exchange-membrane-electrolysis; https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2020/Dec/IRENA_Green_hydrogen_cost_2020.pdf | 也可用 40,000-80,000 小时约束
设备寿命 | 储氢寿命 | h2_storage_life_years | 年 | 20 | 15-30 | web source / second group: Hydrogen Storage and Transport: Technologies and Costs | https://escholarship.org/content/qt83p5k54m/qt83p5k54m_noSplash_8bb1326c13cfb9aa3d0d376ec26d3e06.pdf | 压力容器需按检验周期校核
设备寿命 | 燃料电池寿命 | fuel_cell_life_years | 年 | 10 | 5-15 | web source / second group: DOE Heavy-Duty Fuel Cell System Cost 2023 | https://www.hydrogen.energy.gov/docs/hydrogenprogramlibraries/pdfs/review24/24004-hd-fuel-cell-system-cost-2023.pdf | DOE 重卡系统耐久目标 25,000h；固定式可更高
财务 | 折现率 | discount_rate | - | 0.06 | 0.04-0.08 | web source / second group: IRENA Renewable Power Generation Costs in 2024; RMI 2024 China Power Market Outlook | https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2025/Jul/IRENA_TEC_RPGC_in_2024_Summary_2025.pdf; https://rmi.org/app/uploads/dlm_uploads/2025/01/final-2024-China-Power-Market-Outlook-10-Key-Trends-for-Market-Players-2501117.pdf | 容量规划年化成本用
设备寿命 | 热泵寿命 | heat_pump_life_years | 年 | 15 | 15-18 | web source / IEA heat pump lifetime | https://www.iea.org/reports/the-future-of-heat-pumps/executive-summary | IEA assumes 15 years for air-to-air and 18 years for air-to-water heat pumps; model uses conservative 15 years
市场机制 | 余电上网价格 | grid_sell_price_cny_per_kwh | 元/kWh | 0.2829 | 0.2-0.45 | web source / second group: RMI 2024 China Power Market Outlook | https://rmi.org/app/uploads/dlm_uploads/2025/01/final-2024-China-Power-Market-Outlook-10-Key-Trends-for-Market-Players-2501117.pdf | 按蒙西煤电基准价/机制电价近似，现货和绿电交易需另行替换
市场机制 | 最大上网容量 | grid_export_limit_kw | kW | 50000 | 0-100000 | web source / second group: Frontiers in Energy Research: heavy equipment manufacturing industrial park IES | https://www.frontiersin.org/journals/energy-research/articles/10.3389/fenrg.2024.1448362/full | 按 200MW 接入能力的 25% 设置，可由并网批复替换
市场机制 | 最大购电容量 | max_grid_import_kw | kW | 200000 | 150000-250000 | web source / second group: Frontiers in Energy Research: heavy equipment manufacturing industrial park IES | https://www.frontiersin.org/journals/energy-research/articles/10.3389/fenrg.2024.1448362/full | 公开案例有 200MW capacity 和 150MW peak demand
市场机制 | 需量电费 | demand_charge_cny_per_kw_year | 元/kW·年 | 393.6 | 374.4-393.6 | web source / second group: 锡林郭勒盟发改委: 内蒙古西部电网销售电价和输配电价公示表 | https://fgw.xlgl.gov.cn/fgw/ywgz/jgsf/jfgs/jggs/2023112710530866099/index.html | 35kV/110kV 31.2元/kW·月，1-10kV 32.8元/kW·月
氢市场 | 外购氢价格 | h2_external_supply_cost | 元/kg | 48.6 | 28-56.4 | web source / second group: 国家能源局: 中国氢能发展报告(2025) | https://www.nea.gov.cn/20250430/96022785b3a747248288ad1c57d3a025/83d863317f2f44edb605348e4de40993.pdf | 消费侧价格作为兜底外购价，生产侧价格作为低值
氢市场 | 售氢价格 | h2_sale_price_reference | 元/kg | 45.7 | 28-56.4 | web source / second group: 国家能源局: 中国氢能发展报告(2025) | https://www.nea.gov.cn/20250430/96022785b3a747248288ad1c57d3a025/83d863317f2f44edb605348e4de40993.pdf | 示范城市群消费侧价作对外售价参考
设备效率 | 天然气低位热值 | gas_lhv_kwh_per_m3 | kWh/m3 | 10.814 | 10.5-11 | web source / second group: 国家发改委工业其他行业企业温室气体核算方法与报告指南 | https://www.ndrc.gov.cn/xxgk/zcfb/tz/201511/W020190905506438889540.pdf | 38.931 MJ/m3 / 3.6
氢能 | 储氢逐时损耗率 | h2_storage_loss_rate_per_hour | - | 4.1667e-05 | 0-0.000208 | web source / second group: Hydrogen Storage and Transport: Technologies and Costs | https://escholarship.org/content/qt83p5k54m/qt83p5k54m_noSplash_8bb1326c13cfb9aa3d0d376ec26d3e06.pdf | Converted from hydrogen_storage_loss_per_day / 24
运维退化 | 电池退化成本 | battery_degradation_cost_cny_per_kwh | 元/kWh throughput | 0.1 | 0.06-0.2 | web source / second group: CNESA Energy Storage Industry White Paper 2024 Summary | https://en.cnesa.org/s/CNESA-Energy-Storage-Industry-WhitePaper-2024Summary-Version.pdf | 按储能成本/可用循环吞吐估算
细化曲线 | 电解槽最小负荷率 | electrolyzer_min_load_rate | - | 0.15 | 0.05-0.3 | web source / second group: IRENA Green Hydrogen Cost Reduction | https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2020/Dec/IRENA_Green_hydrogen_cost_2020.pdf | 碱性 15%-100%，PEM 可更宽
氢能 | electrolyzer segment 1 min rate | electrolyzer_segment_1_min_rate | - | 0.15 |  | web source / second group: DOE Technical Targets for PEM Electrolysis; IRENA Green Hydrogen Cost Reduction | https://www.energy.gov/cmei/fuels/technical-targets-proton-exchange-membrane-electrolysis; https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2020/Dec/IRENA_Green_hydrogen_cost_2020.pdf | Piecewise electrolyzer load-rate lower bound
氢能 | electrolyzer segment 1 max rate | electrolyzer_segment_1_max_rate | - | 0.3 |  | web source / second group: DOE Technical Targets for PEM Electrolysis; IRENA Green Hydrogen Cost Reduction | https://www.energy.gov/cmei/fuels/technical-targets-proton-exchange-membrane-electrolysis; https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2020/Dec/IRENA_Green_hydrogen_cost_2020.pdf | Piecewise electrolyzer load-rate upper bound
氢能 | electrolyzer segment 1 kWh per kg | electrolyzer_segment_1_kwh_per_kg | kWh/kgH2 | 60 |  | web source / second group: DOE Technical Targets for PEM Electrolysis; IRENA Green Hydrogen Cost Reduction | https://www.energy.gov/cmei/fuels/technical-targets-proton-exchange-membrane-electrolysis; https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2020/Dec/IRENA_Green_hydrogen_cost_2020.pdf | Piecewise electrolyzer electricity consumption
氢能 | electrolyzer segment 2 min rate | electrolyzer_segment_2_min_rate | - | 0.3 |  | web source / second group: DOE Technical Targets for PEM Electrolysis; IRENA Green Hydrogen Cost Reduction | https://www.energy.gov/cmei/fuels/technical-targets-proton-exchange-membrane-electrolysis; https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2020/Dec/IRENA_Green_hydrogen_cost_2020.pdf | Piecewise electrolyzer load-rate lower bound
氢能 | electrolyzer segment 2 max rate | electrolyzer_segment_2_max_rate | - | 0.6 |  | web source / second group: DOE Technical Targets for PEM Electrolysis; IRENA Green Hydrogen Cost Reduction | https://www.energy.gov/cmei/fuels/technical-targets-proton-exchange-membrane-electrolysis; https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2020/Dec/IRENA_Green_hydrogen_cost_2020.pdf | Piecewise electrolyzer load-rate upper bound
氢能 | electrolyzer segment 2 kWh per kg | electrolyzer_segment_2_kwh_per_kg | kWh/kgH2 | 55 |  | web source / second group: DOE Technical Targets for PEM Electrolysis; IRENA Green Hydrogen Cost Reduction | https://www.energy.gov/cmei/fuels/technical-targets-proton-exchange-membrane-electrolysis; https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2020/Dec/IRENA_Green_hydrogen_cost_2020.pdf | Piecewise electrolyzer electricity consumption
氢能 | electrolyzer segment 3 min rate | electrolyzer_segment_3_min_rate | - | 0.6 |  | web source / second group: DOE Technical Targets for PEM Electrolysis; IRENA Green Hydrogen Cost Reduction | https://www.energy.gov/cmei/fuels/technical-targets-proton-exchange-membrane-electrolysis; https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2020/Dec/IRENA_Green_hydrogen_cost_2020.pdf | Piecewise electrolyzer load-rate lower bound
氢能 | electrolyzer segment 3 max rate | electrolyzer_segment_3_max_rate | - | 0.9 |  | web source / second group: DOE Technical Targets for PEM Electrolysis; IRENA Green Hydrogen Cost Reduction | https://www.energy.gov/cmei/fuels/technical-targets-proton-exchange-membrane-electrolysis; https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2020/Dec/IRENA_Green_hydrogen_cost_2020.pdf | Piecewise electrolyzer load-rate upper bound
氢能 | electrolyzer segment 3 kWh per kg | electrolyzer_segment_3_kwh_per_kg | kWh/kgH2 | 51 |  | web source / second group: DOE Technical Targets for PEM Electrolysis; IRENA Green Hydrogen Cost Reduction | https://www.energy.gov/cmei/fuels/technical-targets-proton-exchange-membrane-electrolysis; https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2020/Dec/IRENA_Green_hydrogen_cost_2020.pdf | Piecewise electrolyzer electricity consumption
氢能 | electrolyzer segment 4 min rate | electrolyzer_segment_4_min_rate | - | 0.9 |  | web source / second group: DOE Technical Targets for PEM Electrolysis; IRENA Green Hydrogen Cost Reduction | https://www.energy.gov/cmei/fuels/technical-targets-proton-exchange-membrane-electrolysis; https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2020/Dec/IRENA_Green_hydrogen_cost_2020.pdf | Piecewise electrolyzer load-rate lower bound
氢能 | electrolyzer segment 4 max rate | electrolyzer_segment_4_max_rate | - | 1 |  | web source / second group: DOE Technical Targets for PEM Electrolysis; IRENA Green Hydrogen Cost Reduction | https://www.energy.gov/cmei/fuels/technical-targets-proton-exchange-membrane-electrolysis; https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2020/Dec/IRENA_Green_hydrogen_cost_2020.pdf | Piecewise electrolyzer load-rate upper bound
氢能 | electrolyzer segment 4 kWh per kg | electrolyzer_segment_4_kwh_per_kg | kWh/kgH2 | 54 |  | web source / second group: DOE Technical Targets for PEM Electrolysis; IRENA Green Hydrogen Cost Reduction | https://www.energy.gov/cmei/fuels/technical-targets-proton-exchange-membrane-electrolysis; https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2020/Dec/IRENA_Green_hydrogen_cost_2020.pdf | Piecewise electrolyzer electricity consumption
细化曲线 | 燃料电池最小负荷率 | fuel_cell_min_load_rate | - | 0.2 | 0.1-0.3 | web source / second group: DOE Heavy-Duty Fuel Cell System Cost 2023 | https://www.hydrogen.energy.gov/docs/hydrogenprogramlibraries/pdfs/review24/24004-hd-fuel-cell-system-cost-2023.pdf | 用于避免小负荷低效运行
氢能 | fuel cell segment 1 min rate | fuel_cell_segment_1_min_rate | - | 0.2 |  | web source / second group: DOE Heavy-Duty Fuel Cell System Cost 2023 | https://www.hydrogen.energy.gov/docs/hydrogenprogramlibraries/pdfs/review24/24004-hd-fuel-cell-system-cost-2023.pdf | Piecewise fuel-cell load-rate lower bound
氢能 | fuel cell segment 1 max rate | fuel_cell_segment_1_max_rate | - | 0.3 |  | web source / second group: DOE Heavy-Duty Fuel Cell System Cost 2023 | https://www.hydrogen.energy.gov/docs/hydrogenprogramlibraries/pdfs/review24/24004-hd-fuel-cell-system-cost-2023.pdf | Piecewise fuel-cell load-rate upper bound
氢能 | fuel cell segment 1 kWh per kg | fuel_cell_segment_1_kwh_per_kg | kWh/kgH2 | 16 |  | web source / second group: DOE Heavy-Duty Fuel Cell System Cost 2023 | https://www.hydrogen.energy.gov/docs/hydrogenprogramlibraries/pdfs/review24/24004-hd-fuel-cell-system-cost-2023.pdf | Piecewise fuel-cell electricity output
氢能 | fuel cell segment 2 min rate | fuel_cell_segment_2_min_rate | - | 0.3 |  | web source / second group: DOE Heavy-Duty Fuel Cell System Cost 2023 | https://www.hydrogen.energy.gov/docs/hydrogenprogramlibraries/pdfs/review24/24004-hd-fuel-cell-system-cost-2023.pdf | Piecewise fuel-cell load-rate lower bound
氢能 | fuel cell segment 2 max rate | fuel_cell_segment_2_max_rate | - | 0.6 |  | web source / second group: DOE Heavy-Duty Fuel Cell System Cost 2023 | https://www.hydrogen.energy.gov/docs/hydrogenprogramlibraries/pdfs/review24/24004-hd-fuel-cell-system-cost-2023.pdf | Piecewise fuel-cell load-rate upper bound
氢能 | fuel cell segment 2 kWh per kg | fuel_cell_segment_2_kwh_per_kg | kWh/kgH2 | 18.5 |  | web source / second group: DOE Heavy-Duty Fuel Cell System Cost 2023 | https://www.hydrogen.energy.gov/docs/hydrogenprogramlibraries/pdfs/review24/24004-hd-fuel-cell-system-cost-2023.pdf | Piecewise fuel-cell electricity output
氢能 | fuel cell segment 3 min rate | fuel_cell_segment_3_min_rate | - | 0.6 |  | web source / second group: DOE Heavy-Duty Fuel Cell System Cost 2023 | https://www.hydrogen.energy.gov/docs/hydrogenprogramlibraries/pdfs/review24/24004-hd-fuel-cell-system-cost-2023.pdf | Piecewise fuel-cell load-rate lower bound
氢能 | fuel cell segment 3 max rate | fuel_cell_segment_3_max_rate | - | 0.9 |  | web source / second group: DOE Heavy-Duty Fuel Cell System Cost 2023 | https://www.hydrogen.energy.gov/docs/hydrogenprogramlibraries/pdfs/review24/24004-hd-fuel-cell-system-cost-2023.pdf | Piecewise fuel-cell load-rate upper bound
氢能 | fuel cell segment 3 kWh per kg | fuel_cell_segment_3_kwh_per_kg | kWh/kgH2 | 19.5 |  | web source / second group: DOE Heavy-Duty Fuel Cell System Cost 2023 | https://www.hydrogen.energy.gov/docs/hydrogenprogramlibraries/pdfs/review24/24004-hd-fuel-cell-system-cost-2023.pdf | Piecewise fuel-cell electricity output
氢能 | fuel cell segment 4 min rate | fuel_cell_segment_4_min_rate | - | 0.9 |  | web source / second group: DOE Heavy-Duty Fuel Cell System Cost 2023 | https://www.hydrogen.energy.gov/docs/hydrogenprogramlibraries/pdfs/review24/24004-hd-fuel-cell-system-cost-2023.pdf | Piecewise fuel-cell load-rate lower bound
氢能 | fuel cell segment 4 max rate | fuel_cell_segment_4_max_rate | - | 1 |  | web source / second group: DOE Heavy-Duty Fuel Cell System Cost 2023 | https://www.hydrogen.energy.gov/docs/hydrogenprogramlibraries/pdfs/review24/24004-hd-fuel-cell-system-cost-2023.pdf | Piecewise fuel-cell load-rate upper bound
氢能 | fuel cell segment 4 kWh per kg | fuel_cell_segment_4_kwh_per_kg | kWh/kgH2 | 18.5 |  | web source / second group: DOE Heavy-Duty Fuel Cell System Cost 2023 | https://www.hydrogen.energy.gov/docs/hydrogenprogramlibraries/pdfs/review24/24004-hd-fuel-cell-system-cost-2023.pdf | Piecewise fuel-cell electricity output
备用价值 | 燃料电池备用容量价值 | fuel_cell_backup_value_cny_per_kw_year | 元/kW·年 | 300 | 100-1000 | web source / second group: LBNL outage cost literature review | https://eta-publications.lbl.gov/sites/default/files/erss_manuscript_preprint_0.pdf | 由停电损失和备用替代成本推导，需实测可靠性校准
备用价值 | 燃料电池备用上限 | fuel_cell_backup_reserve_kw | kW | 10000 | 0-50000 | second group model setting | https://eta-publications.lbl.gov/sites/default/files/erss_manuscript_preprint_0.pdf | Reserve capacity cap used by current second-group run script
备用价值 | 燃料电池必要备用 | fuel_cell_backup_required_kw | kW | 0 | 0-50000 | second group model setting | https://eta-publications.lbl.gov/sites/default/files/erss_manuscript_preprint_0.pdf | Default not mandatory; set by critical-load requirement when available
备用价值 | 停电损失 | value_of_lost_load_cny_per_kwh | 元/kWh | 55.2 | 15-350 | web source / second group: LBNL outage cost literature review | https://eta-publications.lbl.gov/sites/default/files/erss_manuscript_preprint_0.pdf | 7.61 USD/kWh * 7.25，工业差异极大
备用价值 | 年停电小时数 | annual_outage_hours | h/年 | 2 | 0.5-10 | web source / second group: LBNL outage cost literature review | https://eta-publications.lbl.gov/sites/default/files/erss_manuscript_preprint_0.pdf | 需用当地供电可靠性报告替换
细化曲线 | 热泵COP冬季 | heat_pump_cop_winter | - | 2.6 | 2.2-3.2 | web source / second group: NASA POWER Hourly API; IRENA Heat Pump Costs and Markets; IEA industrial heat pump chart notes | https://power.larc.nasa.gov/api/temporal/hourly/point?parameters=ALLSKY_SFC_SW_DWN,WS50M,T2M&community=RE&longitude=109.78&latitude=39.61&start=20240101&end=20241231&format=JSON&time-standard=LST; https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2022/Nov/IRENA_Heat_Pumps_Costs_Markets_2022.pdf; https://www.iea.org/data-and-statistics/charts/energy-input-cost-ratio-of-industrial-heat-pumps-relative-to-current-market-benchmarks-in-selected-regions-2024-3 | 低温空气源热泵按气温下修
细化曲线 | 热泵COP夏季 | heat_pump_cop_summer | - | 4 | 3.5-4.5 | web source / second group: IRENA Heat Pump Costs and Markets; IEA industrial heat pump chart notes | https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2022/Nov/IRENA_Heat_Pumps_Costs_Markets_2022.pdf; https://www.iea.org/data-and-statistics/charts/energy-input-cost-ratio-of-industrial-heat-pumps-relative-to-current-market-benchmarks-in-selected-regions-2024-3 | 夏季/过渡季低温差